# FSM Index:

The FSM Index provides a consolidated view of the key elements that ensure the integrity, reliability, and governance of Safety Instrumented Functions (SIFs) throughout their lifecycle. This index integrates the organization’s main performance and compliance pillars, offering a structured approach to monitoring operational readiness, design conformity, workforce competency, and functional safety requirements.

It encompasses four core components: the Proof Test Index, which evaluates the execution and effectiveness of periodic SIF testing; the Training Matrix Adherence, which measures personnel competency against mandated training requirements; the SIF Design, which tracks deviations and ensures alignment between installed configurations and design assumptions; and the SIF Studies, which centralize all engineering analyses, assessments, and documentation essential to sustaining SIF performance. Together, these elements provide a comprehensive framework for maintaining functional safety excellence and supporting informed decision-making.

- SIF Proof test Index

- Training Matrix Adherence Index

- SIF Design Index

- SIF Studies Index

Threats Index

Indicator that does not impact the FSM index. It serves as predictive information intended to support early detection of potential issues. The Threat Index is based on scenario-change analyses derived from HAZOP reviews that may lead to modifications in the SIF design. The indicator will present the number of scenarios under evaluation and in general it can impact on the SIF design index and the SIF Studies Index.

SIF Proof Test Index

Purpose:

The Proof Test Index (PTI) is a performance indicator designed to monitor compliance with the planned proof test activities for Safety Instrumented Functions (SIFs), in accordance with the requirements of IEC 61511, Clause 11.9, which mandates systematic execution, documentation, and verification of proof tests to ensure SIF integrity throughout the operating phase.

The objective of this index is to:

- Evaluate the timely execution of scheduled proof tests.

- Detect systemic issues affecting SIF availability and reliability.

- Highlight overdue tests, temporary mitigations, and Failure Assurance Activities (FAAs) that indicate deficiencies in functional performance.

- Provide actionable insights for Operations, Asset Integrity team and Reliability Team to maintain ALARP risk levels and ensure continuous compliance.

This index may be further segmented by SIL level, enabling prioritization of overdue or degraded SIFs based on their risk reduction requirements.

SIF Work Orders Execution (Overdue)

This indicator is designed to quantify the EXECUTION of the Work Orders. If the order is mitigated without the test being performed, the index will continue to be impacted. However, if the proof test was carried out and a failure was detected preventing the test from being completed, in that case the index will not be impacted.

Inputs:

The Proof Test Index relies on the following data sources:

- IFS – Work orders, proof test schedules, assurance activity results, FAA generation, and mitigation records.

- Operational Assurance (OA) protocol

Proof Test Compliance Indicator (PTCI%):

The Proof Test Compliant Index (PTCI) measures adherence to the monthly proof test plan based on the original date.

Calculation:

PTCI %=[1-overdue WO proof teststotal proof tests in the month x 100]

Interpretation:

- 100% = Full compliance; all P1 proof tests performed within interval.

- Values < 100% indicate overdue activities reducing SIF availability.

- Can be broken down per SIL category to highlight criticality.

Outputs:

- Execution Index (%)

- Number of overdue and mitigations SIFs by SIL rating

Actions:

- Execute the proof test immediately.

- Mitigation Procedure

Mitigations:

A temporary risk reduction measure is adopted when SIF is unavailable or overdue. O procedimento de mitigação altera a data da WO para uma data futura deixando de contabilizar no planejamento daquele mês.

Inputs:

- IFS

- ORA (when mitigations affect SIF availability)

- Audit records

Calculation:

MCI %=[1- Number of mitigation Proof Test WO not executed x 100

Outputs:

- Monthly Mitigation Index (%)

- List of mitigations activated

- Mitigation recurrence within the last 12 months

Actions:

- Identify recurrence of mitigations for the same SIF.

- Assess mitigation quality, ensuring compensating measures maintain risk at ALARP levels.

- Evaluate whether repeated mitigations indicate design issues, equipment degradation, maintenance gaps, or procedural failure.

- Trigger RCA when recurrence surpasses thresholds or impacts SIL availability.

Failure Assurance Activity (FAA)

Inputs:

- IFS

- Audit records

Calculation:

FAAI %=[1- Number of open FAAtotal proof tests in the monthx 100]

Outputs:

- FAA Index (%)

- List of FAA events and associated equipment

- Required RCAs (5 Whys or more advanced techniques)

Actions:

- Conduct Root Cause Analysis using at least the 5 Whys methodology, escalating to TapRoot or equivalent when necessary.

- Evaluate whether FAA occurrences indicate:

  - Improper test execution

  - Equipment degradation

  - Systematic failures within the assurance activity process

- ORA must be performed when FAA affects SIF availability or leads to degraded mode of operation.

| Metrics | Input | Calculation | Outputs | Action |
| --- | --- | --- | --- | --- |
| SIF Work Orders Execution (Overdue+ Mitigation) (IEC61511-1 clausure 11.9) | - IFS - Audit | - Proof Test Compliant Index Monthly (%): PTCI %=[1-wo not executed proof teststotal WO proof tests x 100] | - Overdue Index Percent - Total overdue SIFs per SIL rate | - Execute immediately or mitigation procedure. |
| Mitigation Index | - IFS - ORA - Audit - MRA | - total mitigations carried out in the month: MCI %=[1- Number of mitigationwo not executed proof testsx 100 The duration of each mitigation will be monitored by comparing the latest date with the due date | - Total activated mitigations carried out in the month index percent - Mitigation recurrence in the last 12 months | - Identify whether there is recurrence of mitigations for the same SIF and assess the quality of the mitigation performed. - RCA - Check the mitigation Quality |
| FAA Quality Index | - IFS | = Number of SIFs in failure / total de sifs do FPSO 9/10 | number of SIFs that are still pending resolution (open FAA) | - Report - |

Table 1: Summary of the proof test index

Training Matrix Adherence Index

Objective:

Evaluate the level of adherence of personnel to the mandatory Training Matrix, ensuring that all critical competencies, certifications, and qualifications are properly updated to guarantee safe operations in compliance with internal, regulatory, and operational integrity requirements.

Inputs:

- List of personnel subjects to the Training Matrix

- Valid certificates issued per employee

- Mandatory training per function, discipline, and criticality

- Training validity dates and frequency

- Official completion records in the corporate system

Calculations:

TMA %=issued certificatesnumber of peoplex 100

Actions:

- Identify gaps in training completion for each category following the training matrix

- Notify personnel and supervisors about upcoming or overdue training.

- Coordinate scheduling of mandatory courses with training providers.

- Ensure certificates are uploaded and validated in the corporate system.

- Monitor expiring certifications and trigger renewal workflows.

- Implement corrective actions when adherence drops below expectations.

- Review Training Matrix periodically to reflect organizational or regulatory changes.

SIF Design Index (Context and Purpose):

The SIF Design section will focus on monitoring:

- Any deviation between the installed system and the original design assumptions, ensuring continuous alignment with Safety Instrumented Function (SIF) requirements and maintaining functional integrity.

Examples include:

- Differences between the as-built logic and the original Cause & Effect matrix (e.g., altered trip setpoints or missing interlocks).

- Installation of field devices (transmitters, switches, valves) with specifications that do not match the approved datasheet (e.g., different SIL rating, response time, or fail-safe action).

- Wiring or loop configuration deviations compared to the design drawings (e.g., incorrect voting logic such as 2oo3 incorrectly wired as 1oo2).

- Control system logic modifications performed during maintenance or troubleshooting that were not reflected in the original SIF design or were not formally approved.

- Replacement of components with different models or firmware versions that could affect the reliability or response time of the SIF.

- Any modification in previously issued documents that requires a design change, ensuring proper traceability, evaluation, and approval of updates impacting SIF performance, lifecycle, or compliance.

Examples include:

- Changes in process conditions that exceed the design envelope assumed in the LOPA or SIL verification (e.g., higher demand rate, increased operating pressure or temperature).

- Changes caused by HAZOP revalidation recommendations, where new deviations or altered operating scenarios require a SIF redesign or additional safeguards.

- Adjustments in engineering specifications or corporate standards (GTS Deviations), prompting alignment with new compliance requirements.

Objective:

The SIF Design Index reports the alignment between the installed configuration of each Safety Instrumented Function (SIF) and the original design assumptions defined during engineering, risk assessment, and SIL verification. Its purpose is to monitor, record, and evaluate any deviations, whether physical, functional, or document-based, that may impact SIF integrity, performance, or compliance.

Inputs:

- GAP Analysis

- Audit

- QnA with change in SIF scenarios

The SDQI% is a structured indicator designed to evaluate the quality and compliance of Safety Instrumented Functions (SIFs) against their Safety Requirement Specifications (SRS). The calculation is based on the principle that each SIF has a defined set of design criteria that must be fulfilled, and each of these criteria contributes differently to overall SRS compliance. Additionally, SIFs with higher SIL ratings carry greater safety criticality and therefore require a proportional weighting factor.

- Checklist-based Compliance Evaluation

Each SIF is assessed through a checklist composed of several design attributes

SIF compliant = Compliance with the SRS

- Loop architecture

- Integrity level of the components

- Installed Partial Stroke Test

- Proof test frequency time OK in the CMMS

- SIFs correctly registered in the CMMS

- Plans correctly registered

- Acceptance criteria

For each criterion, two values are defined:

- Criterion weight (wᵢ): Represents the relative importance of that design aspect

  - SIL 1 = 1,0

  - SIL 2 = 1,5

  - SIL 3 = 2,0

- Criterion score (Iᵢ): A binary evaluation:

  - 1 = compliant (meets SRS requirements)

  - 0 = non-compliant (CMMS/field installation differs from SRS)

Calculations and Metrics:

| Description (SRS Adherence) | Acceptance Criteria | Response (Y/N) | Weight |  |
| --- | --- | --- | --- | --- |
| Loop architecture | Any deviation from the loop diagram? | Y | 2.0 |  |
| Integrity level of the components ok | Any component installed with an integrity level lower than the SRS? | Y | 2.0 |  |
| Installed Partial Stroke Test | Is the proof test frequency in accordance with the SRS? | Y | 3.0 |  |
| Proof test frequency | Is the proof test frequency in accordance with the SRS? | Y | 1.5 |  |
| SIFs correctly registered in the CMMS | Is the SIF correctly registered in the CMMS? | Y | 1.0 |  |
| Plans correctly registered | Is the plan correctly registered in the CMMS? Is the execution procedure attached to the plan? | Y | 1.0 |  |
| Acceptance criteria correctly registered | Is the SIF work order classified as AA, and are the acceptance criteria included in the work‑order closure workflow? | Y | 1.0 |  |

TMA %=1-SIFs compliantTotal of SIFsx 100

Ongoing Assessments Reporting

Ongoing assessments (e.g., HAZOP reviews, GTS alerts, and similar evaluations) will be reported under the Threats Index. This ensures that any emerging risks, deviations, or identified weaknesses are properly captured, tracked, and monitored as part of the site’s systematic threat-management process.

SIF Studies

The SIF Studies section will consolidate all documents, evaluations, and engineering analyses related to the lifecycle of Safety Instrumented Functions (SIFs).
This index will serve as the central repository for tracking functional integrity, design assumptions, operational performance, and any deviations associated with each SIF throughout its lifecycle.

Inputs:

- GAP Analysis

- Audit

Documents:

- SRS

- SIL Verification

- Functional Safety Plan

- Training Matrix

Document Status Metric

Each document will be evaluated according to the following scale:

- Does not exist – 0%

- Exists but is outdated – 50%

- Minor updates pending – 75%

- Up to date – 100%